SOVEREIGN AI WORKBENCH — CONFIDENTIAL DELIVERABLE
MAINTENANCE APPROVAL NOTE

| APPROVAL NOTE ID: | MAN-2026-CE045B |
| --- | --- |
| DATE / TIME: | 2026-08-25 14:09:59 UTC+05:30 |
| TARGET EQUIPMENT: | Boiler Feedwater Pump B-102 |
| SOURCE INSPECTION DOC: | Pump_Inspection_Report_07.pdf |

# 1. Executive Summary & Critical Findings

Vibration level reached 7.8 mm/s RMS on drive-end bearing housing, exceeding operating limits.

CRITICAL ALERT: ISO 10816 Class II threshold exceeded (7.8 mm/s RMS). Immediate category 2 LOTO isolation required.

# 2. Recommended Maintenance Work Orders

Execute LOTO isolation procedure on Feedwater Isolation Valve HV-104 and Pump B-102 power feeder.

Dismantle and inspect drive-end bearing sleeve B-102-BRG for fatigue fractures.

Flush and clean Suction Strainer ST-01 to restore NPSH available.

Perform post-overhaul vibration diagnostic and re-calibrate pressure sensor PT-208.

# 3. Local RAG Evidence Citations

[SOP_Pump_Maintenance_2025.pdf — Page 1]:
"STANDARD OPERATING PROCEDURE
SOP-Pump-Maintenance-2025: High Vibration Overhaul Protocol
Document Ref: SOP-PLANT-2025-V4 | Effective Date: Jan 15, 2025
Section 4.2 Emergency Overhaul Thresholds
Whenever measured vibration on high pressure feedwater pumps exceeds 7.0 mm/s RMS, maintenance engineers
must immediately trigger a Category 2 Emergency Shutdown.
Required Overhaul Steps:
1. Obtain formal Maintenance Approval Note signed by Maintenance Lead.
2. Verify LOTO isolation on high pressure feedwater valves HV-104 and pump power unit.
3. Clean and backflush Suction Strainer ST-01.
4. Inspect sleeve bearing B-102-BRG for tolerance wear and replace sleeve if clearance > 0.15mm."

[Pump_Inspection_Report_07.pdf — Page 1]:
"CONFIDENTIAL INDUSTRIAL INSPECTION REPORT
Equipment Inspection Report #07 — Boiler Feedwater Pump B-102
Date: August 24, 2026 | Inspector: R. Sharma, Senior Diagnostics Specialist
Facility: SRM/SIH Thermal Power Unit — Zone 4 High Pressure Loop
1. Operational Baseline & Telemetry Data
Boiler Feedwater Pump B-102 underwent routine vibration analysis and thermal imaging following scheduled
operational hour threshold (4,500 hours).
Vibration Analysis Findings:
Vibration level measured at 7.8 mm/s RMS on drive-end bearing housing (B-102-BRG). This significantly exceeds the
ISO 10816 Class II alert threshold of 4.5 mm/s RMS and mandatory action threshold of 7.0 mm/s RMS.
Thermal Imaging & Cavitation Observations:
Thermal camera spectrum recorded temperature of 88.4°C on drive-end sleeve casing. Acoustic emissions detect
clear cavitation spikes within impeller stage 2 due to restricted inlet flow at Suction Strainer ST-01.
2. Criticality Assessment & Action Plan
CRITICALITY RATING: HIGH (Category 2 Alert). Continued operation poses severe risk of catastrophic bearing
seizure and impeller destruction. Mandatory maintenance clearance required immediately."

[Safety_Procedure_Plant_Zone4.pdf — Page 1]:
"ZONE 4 PLANT SAFETY INSTRUCTIONS
Safety Procedure: High-Pressure System Isolation & LOTO
Scope: Applies to all maintenance personnel operating in Zone 4 High Pressure Feedwater Loop.
Lockout / Tagout (LOTO) Mandatory Protocol
Prior to opening any pump casing or valve housing in Zone 4, personnel must lock out Valve HV-104 and verify zero
hydraulic line pressure on Transducer PT-208. Safety padlocks must remain locked until final clearance."

# 4. Authorizing Signature & Governance

| PREPARED BY (LOCAL AI): | HUMAN APPROVER SIGN-OFF: |
| --- | --- |
| VAJRA Sovereign Agent Engine v1.0 [Zero Cloud Network Egress Verified] | Approved by: Senior Operations Lead Status: VERIFIED & EXECUTED Timestamp: 2026-08-25 14:09:59 |